## Table 1
OP-020.4 Final Design Documents Checklist
Date:
| Project Name: |  |  |  | Project No:
This checklist is to solely be used as a guideline. Some items may not be applicable.
Project Manager to check first box when this item applies to their project at the beginning of the Contract Documents phase of
the work. Project Manager to review design development package upon completion of phase. Quality Control reviewer to check
second box to confirm that item has been provided.
Architectural Drawings
Cover Sheet
Name of Project
Name of Project Owner
Name of Architect
Project Location (include address, city, state, etc., if known)
Date (must match date on drawing title blocks)
Rendered Building Elevation
Project Number (when Owner has a project number this also should be included)
Right side margin includes project name, project number, and issue date.
Description of drawing purpose (i.e., Construction Documents, Bid Package, Record Drawing).
Information Sheet
Code Analysis completed and up to date
Parking analysis has been included.
Drawing index has been coordinated with actual final sheets in set for all Architectural and consultant
drawings
Vicinity Map
List of abbreviations
Drawing symbols
Project Team list including Owner, Architect, and Consultants names, addresses, phone and fax numbers
and e-mail address
Site Plans
Building footprint with overall building dimensions matching building floor plans. Building plan should be shown as profile of plan where it touches the ground, not a roof plan to allow for showing of improvements under roof overhangs.
Property lines are shown and match civil drawings.
Dimensions of major site elements are coordinated with Civil drawings.
North arrow is shown in the proper orientation.
Graphic scale is provided
Grading and drainage have been reviewed to determine if all areas of the site properly drain and that
steps are provided where grade conditions require.
Site plan has been coordinated with landscape drawings where applicable, including water point of
connection power to controller.
Site plans for Civil, Landscape, Electrical and Architectural have been coordinated and background
electronic copies have been forwarded to each showing final layout.
Details of the following site improvements have been referenced properly.
Trash enclosures
Flagpoles
Screen walls and Retaining walls
Playground equipment
Fencing and gates
Pipe bollards
Loading docks
Site stairs and ramps.
Splash blocks at roof drain outlets
Check to see that differing areas of hardscape pavement are clearly shown as to the type, thickness
limits, scoring and special finishes have been noted and that each is properly referenced in the
specifications
Site furnishings, benches, trash receptacles, and ash urns are shown and detailed or specified.
Parking lot and other site lighting has been shown on the Architectural site plan
Electrical transformers have been shown.
On-site fire hydrants have been shown.
Verify ADA access route is shown on the plan and that slope does not exceed required maximums.
Handicapped parking is properly shown including van access spaces.
Handicapped parking has been referenced to site detail sheet.
On public works projects, approved power, telephone, gas, and off-site improvement drawings must be
in hand prior to bidding.
Fire department access route is provided and coordinated with civil drawings.
Differentiate between new work and existing work to remain.
Site Details: The following site details have been included:
Trash enclosures
Flagpoles
Screen walls and Retaining walls
Playground equipment
Fencing and gates
Pipe bollards
Loading docks
Handicapped parking spaces
Handicapped parking signage
Curb cuts
Site stairs and ramps.
Stair details
Handrail and guardrail details
Special site details not indicated above.
Parking bumper
Exiting Plans
Overall floor plans of each floor level of the building are shown
Fire rated walls are clearly indicated showing scope and appropriate rating. Graphically differentiate
between walls of different ratings.
Number of occupants shown in each occupied space
Number of occupants exiting through exit access doors is indicated.
One half diagonal dimension is shown on plans in spaces where it is not obvious that this requirement
has been met.
Width of stairs is indicated and compared to occupant load served.
Locations of fire extinguishers shown with 45' radius circle at each indicating that entire building area
is covered.
Horizontal exits, exit enclosures and exit passageways have been clearly delineated and labeled.
In high-rise buildings, exit stairs have been provided with vestibules.
North arrow is shown with graphic scale.
Floor Plans
Dimensioning has been properly provided and tied to building grid lines.
North arrow and drawing scale is provided.
Cross reference all detail and interior elevation references against details drawn.
All doors have been numbered appear on the door schedule.
Roll-up doors have been numbered and included in the door schedule.
Partition types designated including the use of the office standard partition type designation.
Operable walls are shown with dashed line to show path of travel and pocket for storing panels is shown
and coordinated with manufacturer for size and layout.
Office standards are being followed as to dimensioning, graphics, lettering, detail referencing, etc.
Cabinets.
All cabinets properly referenced on floor plans or large scale plans.
Cabinet elevations match floor plan for proper overall dimensions.
All rooms and spaces designated with a room name and number.
Stairs have been numbered and referenced to detail sheets in accordance with office standards
Elevators have been numbered and referenced to detail sheets in accordance with office standards
All windows have been noted with Window type.
Fire shutters have been indicated and referenced to details
Large scale plans of special rooms (toilets, etc.) have been referenced.
Built-in elements, such as lockers, display cases, and major equipment, have been shown and details
are referenced.
Tilt-up wall panels have been numbered, shown, and match the structural numbering system.
CMU control/expansion joints have been shown and detailed. Locations are coordinated with
architectural features of the elevations.
Details of special construction conditions have been referenced.
Wall section cuts are provided in proper locations and directions
Building section cuts are provided in proper locations and directions.
Drinking fountains have been shown and coordinated with both plumbing and electrical drawings.
Legend has been provided indicating wall types, window types, doors, finishes, equipment and other
special designations and where additional information can be found.
General Plan Notes have been provided and edited properly to reflect actual project conditions.
Match lines are shown where floor plans have been split into multiple areas.
Room signage information is provided at restrooms, electrical rooms, telephone rooms, etc., where
required by code.
Building expansion joints are shown, and scheduled to referenced details and type.
Mechanical, plumbing and electrical chases are shown and coordinated with MEP drawings for size and
location.
Where required, the following items have been shown and detailed.
Fire Extinguisher cabinets
Floor drains
Louvers
Roof drain downspouts
Display Cabinets, Building Directories, Bulletin Boards
Chalk or Marker boards
Chair rails
Access flooring and associated ramps, steps, rails, etc.
Toilet partitions
Lockers and benches
Shelving units
Janitor sinks with mop holders. Referenced to tile backing detail
Telephone booths
Roof ladders
Walk-off mats
Wall and comer guards
Wardrobe and closet specialties
Equipment layouts are shown in mechanical, electrical, telephone and elevator equipment rooms in a
general outline and coordinated with the consultant's documents.
Large Scale Floor Plans
Toilet Rooms
Detailed dimensions of plumbing fixtures shown and tied to structural grid line
Accessibility clearances are shown with 5' diameter circle and rectangular spaces in front of
sinks and clear dimensions indicated in H/C toilet stalls.
Toilet accessories are all shown and tagged with appropriate letter designation
Toilet stalls and urinal screens are shown and dimensioned.
Grab-bars are shown where required.
Recessed accessories have been coordinated with the required depths of the walls.
Toilet Accessory Schedule is provided and coordinated with plans.
Number and locations of fixtures have been coordinated with plumbing plans.
Floor drains shown and slope to drain indicated.
Locker Rooms
Locker layouts, showing the number of lockers, drawn to scale.
Locker benches are shown
Shower enclosures have indicated accessibility features, such as seats, grab bars, ½" inch recess
at edge, sized in accordance with ADA limitations.
Shower enclosures sizes are in accordance with ADA standards.
Shower accessories such as curtains, curtain rods, soap dishes/dispensers.
Floor drains shown and slope to drain indicated.
Detail has been provided for shower threshold.
Where shower/locker rooms exist in above grade floors, provide waterproof details outside
shower under floor tile.
Detail shower floor receptor and waterproofing.
Reflected Ceiling Plans
Ceiling types are clear as to limits and type and properly referenced and are they consistent with
room finish schedule.
Each ceiling area has a height designation either on this plan or in finish schedule.
Light fixtures are shown and coordinated with the electrical drawings.
Mechanical grilles and diffusers are shown and coordinated with mechanical drawings.
Any special sound-rated or fire-rated ceilings have been properly noted.
Outside soffits and eaves have been shown.
Expansion joints shown and properly referenced.
Building section cuts are shown on RCP's that match the floor plans
Reflected ceiling plan matches the floor plan.
North arrow and scale is shown.
Special ceiling conditions are properly detailed and referenced.
Soffit details have been referenced.
Spaces open to floors above have been noted
Where light fixtures are installed in hard lid ceilings, fixtures are to be dimensioned.
Ceiling finishes and materials are coordinated with finish schedules.
Insulation to be installed on top of ceilings is clearly delineated.
Where tunnel construction for rated corridors, cross hatch the extent of the tunnel.
Legend of ceiling finishes and fixtures is provided.
Attic vents have been shown and detailed when they occur within exterior soffit areas.
Where required, the following items have been shown and detailed.
Projection screens
Rolling grilles
Operable wall and partition tracks
Ceiling mounted television brackets.
Dropped acoustical baffles
Skylights
Roof hatches and access well if required.
Kitchen exhaust hoods
Ceiling hung toilet partitions
Drapery pockets
Steam traps
Draft stop locations
Crown moldings
Gypsum board control joints dimensioned, properly spaced, and detail referenced.
Roof Plan
Slopes are shown and designated to be a minimum ¼'' per foot.
Roof material clearly noted and is it consistent with specified systems.
Crickets shown where needed (including behind large rooftop units).
Proper access to the roof by means of door, roof hatch, or ladder.
Roof drains and overflow drains shown and properly detailed and coordinated with plumbing drawings.
All roof edge conditions have been detailed and referenced and that details are consistent with good
roofing practices and specified materials.
Mechanical equipment has been shown and coordinated with Mechanical drawings.
Equipment curbs are detailed and referenced.
All large roof penetrations have been noted on structural drawings with properly reinforcing angles and
supports.
See that skylights have been properly shown and referenced by correct detail and locations are
dimensioned and coordinated with structural drawings.
Walk way pads are shown and extend from the roof access point (ladder, hatch, door, etc.) to all major
roof top equipment.
Deck bearing elevations are shown at all key grid lines of the roof to indicate slope built into the structure.
Building and wall sections cuts are shown on roof plan and match floor plans.
Roof Details
A standard detail has been included for all penetrations through the roof membrane, including:
pipes
roof drains
conduits
ducts
roof hatch/ladder/safety post
skylights
smoke vents
boiler vents (these require different details then cold vent pipes)
A standard detail has been included for all penetrations through the roof membrane, including:
Details are consistent with good practice and roofing material specified.
Details of roof perimeter are included
Roof equipment screens are detailed, including penetrations through roof membrane.
Roof system assembly is clearly indicated within the details and coordinated with specification
requirements
Exterior Elevations
Building elevations should show the primary building structure. Other elements of the project that may
hide the primary building structure have been removed from the elevation and drawn separately.
All openings, such as windows, doors, louvers, etc., are consistent with plans and frame type indicated.
Materials shown:
Properly designated and noted with reference material, type, paint color, texture, etc.
The limits of each material, color, or texture is clearly indicated.
Ensure that finished floor elevations have been indicated.
Vertical dimensions are shown. Have items requiring vertical dimensions been addressed?
Grading line against the building has been coordinated with the grading plans.
Foundations are shown below grade as a dashed line and generally coordinated with the structural
drawings.
All exterior wall surfaces have been elevated, including return walls, free standing arcade panels, and
other wall surfaces not normally shown on the major building elevations. Some of these surfaces may
appear in the background of wall sections which is acceptable, so long as surface finishes are called out.
The following elements are shown, referenced, and called out:
Reveals in surface materials.
Control joints in masonry work
Parapet caps
Louvers (coordinated with mechanical)
Exterior building mounted light fixtures (coordinated with electrical)
Building structural gridlines (there is no need to dimension these on elevations, it is just a duplication of
the information already provided on floor plans).
Complex areas of exterior elevations have been enlarged to an appropriate scale for clear understanding
of the intent of the work.
Indicate building and wall sections cuts on exterior elevations.
Building Sections: (Building sections are provided to give the contractor a general view of the intent of the
building construction and arrangement. They are not intended to show details, interior elevations, finishes,
interior doors, etc. These drawings are generally very simple views.)
A minimum of one longitudinal and one lateral building section have been drawn. More
complex buildings may require more.
Top of slab floor elevations are indicated.
Floor to floor dimensions are indicated.
Equipment screen walls are shown on sections.
Building structure is shown correctly and coordinated with structural. (Joists are shown as joists, wide
flange beams are shown as wide flange beams, etc.)
Roof is shown properly sloped and coordinated with roof plan.
Wall sections have been referenced.
Wall Sections
Sections have been drawn for all appropriate areas of the building.
Structural elements of the building have been shown correctly scaled to actual size.
Exterior wall construction has been shown and connections to roof, floors and grade are referenced to
large scale details.
Building insulation is shown
Sections are drawn to full height of parapet.
Floor elevations are indicated and coordinated with building sections.
Bracing to structure has been shown and called out where required.
Safing insulation has been shown at floor edges where required.
Building grid lines are shown
Dimensions from grid lines to edge of slab and to exterior face of stud/masonry are provided.
Fireproofing of steel is shown where required.
Wall assembly has been shown and all relevant materials called out.
Waterproofing or dampproofing is shown where occupied spaces occur below grade.
Interior ceilings are shown
Dimensions from floor to bottom of window or other elements is indicated.
Where masonry walls are shown, block coursing is indicated.
Wall sections cuts are shown on floor plans and exterior elevations
Tilt-up Panels
Elevations of every panel has been provided
Every panel has a panel number and is consistent with the structural panel number.
Overall height of panel is indicated as measured from level one finished floor.
Panel widths are dimensioned, including width of panel joints.
Openings are shown and dimensioned from finished floor line and edge of panel.
Recessed areas of panels are clearly delineated and depth from face of panel indicated.
"V" groove reveals are shown and dimensioned.
2" wide panels reveals are shown and dimensioned.
General panel notes are provided.
Typical Panel Detail reference box is provided.
Typical panel details are provided
Non-typical panel details are provided and referenced on panel elevations.
Special finish treatment areas of panel faces has been delineated (sandblast, exposed aggregate, etc.)
Section, Column and Wall Details
Office standard details have been used wherever possible.
Sections are provided and referenced for the following conditions (some details may be provided as a
part of other portions of the work, such as roof or door details):
Wall at foundation connection
Wall at intermediate floor
Wall at roof line
Top of parapet
Roof edge
Window sill
Window head
Door threshold
Door head
Clerestory window
Notes on details use proper abbreviations, terminology, and consistency with specified materials.
The scale of the details shown.
Are details consistent with structural drawings?
Dimensions are adequate, correct, and tied to grid lines where appropriate.
The detail makes sense, is compatible with construction materials of building and is buildable.
Door Schedules
Door schedule includes all doors including interior, exterior, roll-up doors, sliding doors, roll-up grilles,
etc. (do not number elevator doors)
Room name associated with the door has been provided.
Door details coordinate with wall types.
Door and window details are consistent with standard practice of the industry.
Door schedule detail references are correctly referenced to details drawn and frame types.
Fire rating when required.
"S" label doors and frames are indicated where required.
Temperature Rise rating is indicated where required.
Hardware schedule number is included.
Special conditions have been noted, such as STC rating, existing door, special finishes, etc.
Frame types indicated consistent with frame type shown on the plan.
Door types indicated and consistent with door type legend.
Door Types
Each different door type has been drawn
Each type has written text information regarding construction (Hollow Metal, Solid Core Wood,
Storefront, Full Glass, etc.)
Door sizes are noted in height and width as "See Schedule"
Where windows, louvers or other openings occur, these have been dimensioned and called out.
Where glass is indicated, note as tempered glass, wire glass or "Fire Lite"
Each door type has a corresponding letter designation.
Door Frame Types: Where doors occur in exterior window systems, and this frame has been drawn as one of
the window types, do not re-draw this as a door frame type. However, in the door schedule, be sure to reference
the appropriate frame elevations within the frame type box.
Each different type of frame has been drawn.
Each frame type has a corresponding number designation.
Where sidelites occur, these have been drawn and dimensioned.
Where sidelites occur, call out the glass as tempered, wire glass or "Fire Lite".
Frame thickness is dimensioned.
Frame sizes are noted in height and width as "See Schedule"
Window Frame Types
Each differing window frame has been drawn
Each window type has been provided with a frame type "W" number designation
Glazing for each opening has been noted. (where the majority of glass is of one type, a note may be
provided in the text of each frame elevation that "All glass shall be glass type XXX unless noted
otherwise".)
Spandrel panels have been designated
Tempered glass has been noted where required
Each frame type has written description of frame material
Glass type schedule has been provided.
Frames have been fully dimensioned, including width of frames, opening sizes and overall frame
dimensions.
Plan view of window elevations are provided where something other than a straight frame is required.
Detail reference bubbles have been provided at frame edges.
Indicate finish of frame in text under window frame elevation.
Finish Schedule
All rooms have been included in the schedule
Room names are included
Schedule includes finishes for each of the following:
Floor
Base
North, South, East and West walls
Ceilings
Remarks include clarifications regarding wainscots, multiple finishes within the same area, references to
interior elevations, etc.
Window treatment is designated (blinds, drapery, etc.) where these items are a part of the scope of the
work.
Finish Legend
Each specific designation of manufacturer, color, style, size, etc., has been provided.
Note at the top of the schedule as follows: "Product manufacturers and color designations listed
below are provided to establish a color, finish or material standard. Products provided by
manufacturers listed in the specifications as an approved manufacturer are acceptable subject to
approval by the Architect that color, texture, finish or material standard is essentially equal to that listed."
Interior Elevations: Interior elevations are to be drawn only where complex or special finishes are required.
All elevations drawn that have been referenced on the floor plan.
Ceiling heights are consistent with schedules and plans.
Cabinet elevations are properly referenced to details.
Millwork elevations:
Fully Dimensioned
Each differing material has been called out by designation to finish legend.
Trim and molding profiles have been referenced
Wall covering or painted finishes are designated.
Crown moldings are shown.
Sections and/or details of special construction have been referenced.
Restroom elevations are provided with plumbing drawings as well as large scale architectural plans.
Toilet accessories shown.
Mounting heights of fixtures.
Special tile designs for wall tile.
Wall Types
Office standard wall types have been utilized.
Rated walls noted are consistent with exiting plan
Reference details for head of wall, and wall penetrations have been filled into the bubbles provided
where required.
Head of wall UL details are included in drawing package.
Wall penetration UL details are included in drawing package.
Rated walls reference either UL or UBC wall assembly number. Where other than UBC assembly is
used, a testing agency detail has been provided.
Stair Plans and Sections
Floor to floor heights are consistent with building sections.
The proper number of risers have been provided and do not exceed 7" as required by the building code.
The stair plan indicates the number and typical dimension of the stair treads, which is not less than 11".
Handrails have been shown and, the height above the risers is between is not less that 34" and not more
than 38".
The spacing of handrails is noted at 1½" away from wall surfaces.
The width of stairs has been noted and is not less than 48" between handrails. Where stairs are required
to be wider than the 48" per the exiting plan, these are shown at the appropriate width.
Where landings exist in a straight run of stairs, this landing is at least 44 inches in the direction of travel.
The width of the stairs is continuous at landings in which the stair changes direction. An arch should be
drawn on the plan to clearly call out this requirement.
Stair runs do not exceed 12' in height without an intervening landing.
Handrail extensions have been clearly indicated showing the 12" horizontal extension at the top and the
one tread plus 12" extension at the bottom.
42" high guardrails are provided where landings are open to spaces below. Guardrails on open side of
the stair are indicated at a height equal to the required height of the handrail.
Where stairs are required to be more than 88" wide, an intermediate rail has been provided.
Clear height headroom above the stairs is greater than 6'-8". This minimum is required by code, but
should be much greater if possible. This is a very low measurement and can feel awkward when
approaching and taller people will tend to want to duck when passing under this low of a clearance.
In buildings four or more stories in height, at least one stair extends to the roof.
Detail bubble references have been provided at standard locations and correctly referenced.
Details have been provided for the following locations:
Landing to upward running stairs.
Landing to downward running stairs
Stringer to wall detail
Typical stair riser
Open landing edge detail
Landing to wall detail
Handrail to wall
Special finishes on stairs, such as rubber treads and risers, carpet, etc., have been noted.
Elevator Plans and Sections
¼" scale plans have been provided for every elevator floor. Where multiple floors are identical, a plan
is provided with notation that this plan is typical for levels __________. Ground floor elevator plan
should always be drawn separately to show pit equipment required.
Elevator plans are dimensioned with clear openings and tied to building grid lines in both directions.
Hoistway entrances are shown properly (i.e., side opening, center opening, front/rear openings, etc.)
Elevator hoistways have proper ventilation through the roof (3 sq. ft. per elevator).
Hoistways are detailed to be built with proper fire ratings.
Hoistway have been properly sized and drawn to accurately show the required width, and depth of the
elevator selected.
Elevator plans show the elevator hoistway in exactly the same location for each floor.
Hoistways for holeless hydraulic, holed hydraulic and traction type elevators are different. The
drawings are properly indicating the correct clearances, equipment and rails required for each type.
Elevator pits depths are indicated in sections and coordinated with requirements of elevator
manufacturer. Remember that holeless elevators will require deeper pits when the run of the elevator
exceeds 13'-7". Usually this is an increase of 1" of depth for every 1" of run that exceeds this run height.
Clearance above the elevator to the roof structure is as required by the manufacturer for each type of
elevator (remember to account for higher than standard ceiling heights in the elevator cab).
In traction type elevators, the elevator machine room has been shown in both plan and section with all
equipment shown and required clearances in front of controllers provided.
In traction elevators, floor openings have been shown and dimensioned.
Clear heights required by elevator manufacturers have been provided in all machine rooms.
In holed and holeless type elevators, the machine room has been provided within the maximum
separation required by the manufacturer.
In holed and holeless type elevators, the machine room has been coordinated with the requirement of
the equipment, controllers, disconnects, etc.
Elevator equipment room is rated as l hour for holed and holeless types, 2 hour for traction elevators
when the hoistway is required to be 2 hour rated.
Elevator cab has been provided to comply with requirements of the ADA.
ADA standard details have been provided.
Detail of the elevator threshold has been provided.
The following items have been provided:
Pit ladder
Pit light
Convenience outlet in pit .
Separator beams between elevators in same hoistway at a not-to-exceed spacing of 14'-0".
These separator beams must also be shown on the structural drawings.
Telephone service to car (verify with electrical drawings)
Sump pump or gravity drain to outside. This is now required for all elevators per elevator
code. Coordinate with electrical and plumbing.
Finishes for elevator cab have been indicated in specification per one of the manufacturers' standards, or
if custom cabs are required, elevations of cabs have been provided.
Elevator sections are correct with the type of elevator being used. For example, if a holed elevator is
required, the plunger sleeve should be shown, for a holeless elevator, it should not.
The wall construction at the hoistway entrances is clearly indicated by correct wall type such that the
manufacturer can clearly understand the depth required for the entrance frame assembly.
Casework
Elevations of all casework has been drawn and properly referenced.
Backsplash has been shown
Elevations indicate section cuts
Section cuts through casework has been provided.
Finishes for each exposed surface of casework has been provided
Dimensions, both vertical and horizontal, have been provided. Remember, horizontal dimensions for
standard casework come in 3" increments.
Height of countertops is in accordance with accessibility standards.
Filler panels have been indicated at cabinet ends where gap may occur between
cabinet and wall surface
Where cabinet locks are required, they should be indicated on elevations.
Cabinet base material is called out as either the same as cabinet face or rubber base.
Ensure that all hardware items have been properly specified.
Where glass doors are required in cabinet doors, these have been shown.
Where equipment is to be provided within or around the cabinets, coordinated opening dimensions have
been provided.
The following items have been noted and referenced as either in contract or NIC.
Under counter refrigerators
Full size refrigerators
Vending machines
Dishwashers
Ice makers
Garbage disposals
Microwave ovens
Regular oven and/or stove tops.
Wine coolers
Under cabinet lighting
Sinks
Undercounter trash receptacles
Built-in computer monitors
Wire grommets in counter tops
Standard details have been provided for the following:
Typical base cabinet
Base cabinet with sink
Base cabinet with drawers
Typical upper cabinets
Restroom sink countertops
Special casework cabinet sections
Structural Drawings
The following areas should be coordinated with the architectural drawings and specifications and as a checklist, to ensure that
these items have been properly provided.
General Structural Notes
All appropriate building materials have been included in the descriptions which may include:
Concrete
Reinforcing Steel
Foundation
Structural Steel
Wood Framing
Concrete Masonry Units
Glu-Laminated Members
Post Tensioned Concrete
Tilt up Concrete
Steel Roof/Floor Deck
Load bearing metal studs
Steel trusses/girders
Wood trusses
"T" Series framing members
Wood Sheathing/Plywood/OSB
Material descriptions match those provided in the specifications.
Concrete for slab-on-grade work is a minimum of 4500 psi strength.
Footing and Foundation Plan
All building and grid lines match locations, grid reference number and dimensions of the architectural
drawings.
Finished floor heights match architectural and civil drawings.
Recessed slabs have been properly designated and limits clear and consistent with architectural drawings.
Verify against the following areas:
Restroom floors where slope is required to drain or when thick-set floor tile is scheduled.
Lobbies and other floor areas where thick-set floor tile or stone is scheduled.
Exterior balconies.
Floor slab assembly, sub-grade, drainage fill, vapor barrier, slab thickness, and reinforcing have all
been called out.
Top of foundation walls been recessed at all architectural door openings and wherever the top of the
foundation wall would not be desirable to be left exposed.
Elevator pit has been correctly located and sized.
Compare outside edges of floor slab with architectural recesses, extensions, and other appurtenances.
Floor control and expansion joints are shown.
Locations and sizes of structural columns have been verified with architectural drawings.
Columns not falling on grid lines have been dimensioned to nearest structural grids.
Braced frames have been coordinated with architectural plans and any penetrations through these
areas, such as doors, windows and ductwork.
Floor Framing Plans
Top of steel elevations and the slab thickness given are consistent with finished floor elevations shown
on the architectural drawings.
Recessed areas of slabs have been shown where they occur on suspended floors and are coordinated
with architectural limitations of the area required.
Openings in floor slabs have been provided for large penetrations, such as duct and air return chases, and
are they located properly?
Detail referencing is consistent with architectural.
Edge of slabs are coordinated with profile of architectural floor surfaces.
Stair landings at floor levels have been shown (stairs and intermediate landings are part of the work of
the stair fabricator).
Openings for stairs and elevators are shown and are consistent with architectural.
Elevator spreader beams have been shown and sized.
Braced frames have been coordinated with architectural plans and any penetrations through these areas,
such as doors, windows and ductwork.
Tilt Up Panels (Structural panels will be drawn looking at them from the inside, while architectural panel
elevations are shown from the exterior side.)
Floor plan panel numbers match those shown on the architectural plans.
Panel elevations are drawn for all panels
Panel elevations match size and configurations of architectural
Panel openings are coordinated with architectural
Reinforcing for openings is clearly indicated
Panel thickness is indicated on drawings and consistent with architectural
Recessed areas of panels have been indicated and coordinated with architectural
Knock-out panels are indicated and appropriately reinforced.
Arcade panels and other non-structural decorative panels have been elevated and detailed.
Roof Framing Plans
Roof slopes built into the structure are consistent with the architectural roof drainage system.
Building grid lines match locations and grid reference number of the architectural
Large openings for skylights, roof hatches, duct penetrations, etc., have been noted and framing detailed
around openings
Details of roof edges are consistent with architectural.
Structural support has been provided for large roof-top equipment and weights of units, and locations are
indicated on the drawings.
Roof top equipment screens are shown, structurally detailed and coordinated with architectural roof plans.
Mechanical Drawings
HVAC
Check against structural and architectural for key locations where conflicts and lack of proper space
may occur.
Building gridlines match locations and grid reference number of the architectural drawings.
Size of rooftop equipment has been verified and is properly screened from view.
Every space is provided with air and that the control for each area is located in an area that is logical and
convenient.
Every restroom has been properly ventilated.
Smoke/Fire dampers have been provided at all fire-rated walls and ceilings, and there are access doors or
accessible ceilings nearby for resetting dampers.
VAV boxes, valves, and other ceiling-located equipment has adequate access for adjustment and future
repair.
Heat pump units inside ceiling spaces have clearances required for filter changes.
Trace back through the return air system from every space to ensure that air movement can properly
take place and, if the architectural shows a wall to structure that may be blocking the path, there is
an opening provided and fire dampered if necessary for the air movement.
Verify that adequate ceiling space is provided for duct work. Coordinate with other known items
in ceiling space such as structural steel, roof drainage systems, etc.
All mechanical equipment has been provided with the appropriate electrical service, disconnects, gas
connections, drains, water supplies, etc.
Area for cooling towers is adequate and is screened from view where required.
Boiler stacks have been coordinated with required clearances around roof penetrations, and shaft walls
have been coordinated through the building when the boiler stack must run through floors above.
Boilers have been provided with enough space for pulling tubes out for future maintenance.
Chillers have been provided with enough space for pulling tubes out for future maintenance.
Chilled and hot water piping has been coordinated with structural for proper support.
Boiler rooms have been provided with a 2-hour fire rating and proper combustion air intakes.
Air grilles have been coordinated with architect's reflected ceiling plans.
Ventilation for elevator hoistways has been shown. (Note: traction elevators will not allow this
ventilation to pass through the machine room, it must be directed past this room outside the space).
Schedule of grilles and other exposed HVAC equipment has been reviewed by architect for appearance
and appropriateness to the ceiling design.
Thermostats have been located in appropriate spaces and have been coordinated with architectural
features, such as windows, doors and sidelites, millwork, markerboards, cabinets or equipment locations.
Rooms containing noisy equipment have been properly sound attenuated from surrounding spaces.
Air handlers have adequate ceiling space above. Review carefully including any sloping structures for
roof drainage.
Rooftop equipment has adequate access for maintenance.
Condensation drain lines are brought to an appropriate outlet in a non-public area.
Heaters have been provided inside fire riser room.
Plumbing Drawings
Water Supply
Plumbing plans are coordinated with toilet room plans; ensure fixture numbers and types are consistent.
Building and grid lines match locations and grid reference numbers of the architectural drawings.
Fire riser has been located and coordinated with architectural and civil
Compare plumbing plans with architectural drawings for:
floor drains
electric water coolers
hose bibbs
custodial sinks
remote plumbing fixture
ice makers
commercial kitchen equipment
residential kitchen equipment
evaporative coolers
Coordinate domestic water supply lines with civil drawings for locations, size, flow lines, etc.
Water heaters have been properly located within maintenance spaces
Plumbing fixture cut sheets have been provided and reviewed by the architect for appearance and
coordination with architectural elements such as casework.
Where automatic faucets and flush valves are used, electrical power has been provided.
Sewer and Storm Drainage
Coordinate sewer lines with civil drawings for location, size, and invert elevation.
Ensure provisions have been made for connections to outside landscaping sprinkler systems and
coordinate location.
Coordinate roof drain lines with civil for connections to storm sewers or for proper flow of daylighted
drains to storm system.
Where under-walk roof drain leaders are used, coordinate with locations where zero curbs will not
occur.
Review roof drainage piping to see that the minimum amount of piping required is provided.
Roof drain laterals have adequate space above ceilings.
Roof drain lines are coordinated to see that they are properly concealed from view in public spaces of
the building, and if they are run down through walls, make sure that wall thickness is adequate to
accommodate the pipe size and hub fittings.
Gas Service
Gas meter has been located and coordinated with architectural, civil, and landscape
Gas meter is located in a logical location away from main public access areas.
Gas service has been provided to the following:
Water heaters
HVAC equipment
Residential stove tops and ovens
Commercial kitchen equipment
Boilers
Unit heaters
Gas drawings have been submitted to Gas Co.
Electrical Drawings
Lighting
Lighting layouts have been coordinated with architectural reflected ceiling plans for quantities and
fixture types.
Building and grid lines match locations and grid reference numbers of the architectural drawings.
Where recessed fixtures are called out, verify that there is adequate ceiling space and potential
conflicts with ducts or structure.
Parking lot lighting is coordinated with architectural landscape and civil drawings
Light switches have been located in convenient locations but coordinated with door sidelights,
marker boards, etc.
Landscape accent lights have been provided with proper documentation
Site light bollards have been provided with proper documentation.
Under counter lights have been shown where required by architect.
Cut sheets of light fixtures have been provided and reviewed by architect and owner.
Pit light and switch has been provided in elevator pit.
Address number is lit according to signage standards.
Power
An adequate number of convenience outlets has been provided.
Electrical outlets that occur above counters have been properly noted to be mounted at proper height.
Building fixtures and equipment have power:
Under counter refrigerators
Full size refrigerators
Vending machines
Dishwashers
Ice makers
Garbage disposals
Microwave ovens
Regular oven and/or stove tops.
Wine coolers
Under cabinet lighting
Under-counter trash compactors
Built-in under-counter computer monitors
Roll-up services doors
Dock levelers
Projection screens
Electric water coolers
Electric water heaters
Mechanical equipment disconnects
Automatic faucets and flush valves
Doors requiring security devices
Television locations
Security cameras
Landscape sprinkler controller
Convenience outlet at telephone board
Smoke/fire dampers
Site monument signs
Address numbers when integrally lit.
Lighted building signs
Lighted bulletin boards
Commercial kitchen equipment
Power-operated entrance doors
Power-operated parking control gates
Site-located parking control booths
Covered parking structure lighting
WP/GFI outlets have been provided on the roof for maintenance of equipment.
GFI outlets have been provided at kitchen and bathroom sinks.
Power for systems furniture has been provided in accordance with manufacturers' requirements.
Electrical panels have been located properly to allow 3' clearance in front and that they do not conflict
with architectural equipment or other obstructions. Also, determine if the wall behind the panel is thick
enough to mount the panel, if a recessed panel is specified.
Electrical room has been provided with two means of egress when space in front of equipment is less
than required distance.
Transformer and meter pads are located in an appropriate location and coordinated with architectural,
civil and landscape drawings.
Drawings have been submitted to the local power utility for their preparation of final power service documents.
Shunt trip switch is located
Electrical meter has been located in accordance with the requirements of the local power utility.
Lightning protection has been provided where required and coordinated with architectural drawings.
Standby or emergency generator has been shown and coordinated with architectural site plan, civil and
landscape drawings.
Adequate sleeving has been provided under pavement to allow for future power access where requested
by Owner.
Mechanical equipment power requirements have been verified.
Auxiliary Plans
Data outlets have been provided in all appropriate locations and have been reviewed by the Owner.
Fire alarm system is shown with the following devices and coordinated with the architectural plans:
Pull stations
Horn strobe lights
Annunciator panel
Fire alarm panel
Smoke detectors
Magnetic hold opens
Telephone outlets have been provided in appropriate locations approved by the Owner and in the
following locations:
Fire Riser
Elevator equipment room for connection to car phones
Pay phone locations
Building security panel
Reception counter
Parking control booth or control equipment
Plans have been submitted to Sprint, XO, or other telephone system supplier.
Telephone backboard is indicated
Cable tray layouts have been shown, penetrations through fire walls are fire-stopped
Security systems have been shown and include the following:
Doors with electronic locks
Architect to verify, on hardware schedule, that appropriate electronic hardware has been
specified.
Cameras have been shown and coordinated with architect's reflected ceiling plans
Card readers have been located where required by Owner
Motion sensors have been shown
Glass break sensors have been shown
Site cameras have been indicated and provided with power where required.
Civil Drawings
Horizontal Control Plan
Dimensions of site improvements match those on architectural site plans.
Parking spaces have been coordinated with architectural drawings.
Location of building is coordinated with architectural drawings.
Locations of off-site work has been dimensioned from property lines.
Widths of fire department access routes are in accordance with local standards (inside radius = 28',
outside radius= 52').
Grading Plan
All areas of site have adequate flow for storm drainage.
Existing and proposed grades/contours are clearly designated.
Underground storm drainage piping has been shown and is coordinated with off-site drainage systems
locations and invert elevations
Connections to roof drainage system has been coordinated with plumbing locations and invert
elevations
Access routes have been provided and verified for the following:
Maximum slope in handicapped parking spaces does not exceed 2%
Accessible route has been provided from parking stalls to building entrances
Cross slope of access routes does not exceed 2%
Access routes do not exceed 5% slope, or where it does, ramps, rails, and proper configuration
of route has been provided.
Drop-off zone slopes do not exceed 2%
Zero curb cuts have been shown at handicapped parking stalls
Curb cuts have been shown on off-site sidewalks where required.
Curb cuts for on-site accessible routes have been provided.
Grade elevations at building access points is no more than ½" below floor slab.
Grades next to buildings are coordinated with floor levels and structural foundations.
Grades next to buildings slope away from building and flow to hard surface areas.
Where retaining walls are required, extent has been shown and detailed.
Structural details are provided for site retaining walls.
Top of curb elevations have been provided at all appropriate locations.
Finished floor elevation has been shown and coordinated with architectural documents
Areas requiring steps are shown and coordinated with architectural site plan
Landscape areas have been coordinated with civil design layouts.
Utility Plans
Connection to public water service has been indicated.
Detector check, RPPA, and backflow preventor have been shown and appropriately located.
Meters have been shown.
Fire lines have been shown and fire hydrants have been coordinated with architectural, landscape and
electrical site plans
Fire line to riser has been coordinated with architectural
Fire Department connections are indicated
Connection to public sewer lines has been indicated
Connection of sewer line to building is shown and location and invert elevation is coordinated with
plumbing drawings.
Connection to landscape irrigation is shown
Easements required by public utilities have been shown and appropriate applications have been made
to necessary parties.
All manholes, drain inlets, etc., have been indicated and detail referenced.
Landscape Drawings
Planting Plan
Locations of trees and other landscape materials have been coordinated with other site improvements
including the following:
Fire hydrants
Parking lot lights
Transformers
RPPA, detector checks
Side walks
Overhead structures
Covered parking structures
Drainage structures, inlets, etc.
Landscape materials have been provided in all areas required
Driveway visibility has been considered in selecting plants at street entrances. Coordinate with civil for
areas of concern.
Trees requiring deep roots (palm trees) are not shown over new or existing underground water, sewer,
telephone or electrical lines.
Each type of planting material is shown by separate symbol.
Planting schedule legend indicates type and quantity of plant materials.
Hardscape Improvement Plans
Hardscape areas are coordinated with architectural and civil drawings
Accessibility has been considered in the design of the hardscape areas.
Finishes of walk surfaces have been clearly delineated as to the type and scope of each.
Grades indicated on hardscape plans are coordinated with civil grading plans.
Irrigation Plans
Point of connection to water supply is shown and coordinated with civil utility plans
Controllers have been shown and coordinated with electrical drawing for power supply
Sleeving under driveways, walks, and paved areas have been provided to allow for future maintenance
and added piping.
Above-ground, spray-type heads do not spray against the buildings. They should be far enough away to
prevent wind-blown spray onto building as well.
All landscape/turf areas have adequate irrigation supply
Irrigation schedule has been provided
Total water and water pressure requirements are provided.
Project Manuals
General Comments
The boiler plate portion of the specification manual should be reviewed generally for completeness,
but specific requirements for the project such as completion date, bidding requirements,
Owner/Contractor Agreements, insurance requirements, and liquidated damages will need to be
worked out by the project manager with the project Owner.
Terminology: ensure that the terms and abbreviations used in the drawings are the same as those used
in the specifications. These should also be in agreement with the abbreviations listed on page A0 of the
drawings. As an example, if the term "gypsum board" or "gyp board" is used in the specs, we will not
accept such descriptions as "sheet rock" or "plaster board" on the drawings. It can be a great benefit to
the project team if a listing of terminology is provided at the beginning of a project.
Definition: Beyond using the proper terminology, it is also important the ensure that a complete
description of a product be made within the body of the specification. For example, when a product
description is used on the drawings, such as "Type II Structural Fill," we would expect to see
Type II Structural Fill in the specifications and an exact designation of what it is (i.e., sieve
analysis, gradation, etc.), as well as description of how it is to be replaced and compacted.
Responsibility: We often find places where the same item is called out in more than one section of the
specifications. For example, door hardware for store front systems is often specified in both the store
front system section as well as the hardware section. This can be true with glass, roof drains, and
compacted base courses under asphalt. These are not as bad as when neither section specifies a
material or both refer to the other as providing something. It should be made clear as to which section
will provide each given product.
Completeness: A review will be made to ensure that a specification has been written for all products
listed on the drawings and that products are specified within a logical section of the specification.